## Slide 1
BiT Tracker Control Unit
Smart Tracking
TCU
Mobile APP
Lora to BlueTooth
NCU.1 Lora Gateway
NCU.n Lora Gateway
TCU.1.1
TCU.1.2
TCU.1.n
n<=200
Transformer
Com Box.1
Transformer
Com Box.n
Wind Sensor.1
Wind Sensor.n
Solar Plant SCADA
GPRS/LTE4G
RS485
LORA
LORA
RS485
FIBER OPTICS
FIBER OPTICS
AC 220V
RS485
AC 220V
RS485
AC 220V from TRS
JuTracker Cloud Platform
LORA
DC 50V~200V from String
Tracking
Astronomical
Backtracking
Sensor Control
Feedback
Power Supply
Angle
Temp
DOD Battery
Communication
LoRa
RS485
Sensor
AC 220V from Trs
DC from String
Protection
Current
Voltage
Angle
Emergency Stop
© Jutracker Inc. Contents subject to change without notice. ALL RIGHTS RESERVED 2021 VER2.0
No 298 Kangyang Road, Xiangchen District, Suzhou, China | www.jutracker.com | sales@jutracker.com

## Slide 2
Jutracker
© Jutracker Inc. Contents subject to change without notice. ALL RIGHTS RESERVED 2021 VER2.0
No 298 Kangyang Road, Xiangchen District, Suzhou, China | www.jutracker.com | sales@jutracker.com
BiT-TCU
Tracker Control Unit Controller Electrical Specifications |  | TCU
Characteristic Parameters |  | 
Input |  | 
String-powered Supply |  | String-powered (50-200V DC)
External Supply |  | LV side Transformer(220V AC)
Output |  | 
Working Voltage |  | DC 24V
Rated Output Current |  | 6A
Max. Output Current |  | 10A
Battery |  | 
Battery Type |  | Lithium-ion Battery
Battery Capactiy (String-powered supply) |  | 6500mAh
Power Consumption |  | 
Daily Energy Consumption |  | 0.2 kWh/Day
Smart Controlling |  | 
Tracking Algorithm |  | SmartTrack
Rainy Cleaning Mode |  | Yes
Snow Mode |  | Yes
Hail Pattern |  | Yes
Wind Protection |  | Multi-Level Wind Protection
Reset Protection at Night Parking |  | Yes
Rotation Limit Protection |  | Yes
Motor Overcurrent Protection |  | Yes
Manual/Automatic Tracking Mode |  | Yes
Emergency Button |  | Yes
General Data |  | 
Certification |  | CE,IEC,TUV
Environment Temperature |  | -40°C ~ 60°C
Tracking Angle |  | Up to ±60°
Tracking Accuracy |  | <±1°
Wireless Communication |  | LoRa
Wire communication |  | RS485
Protection Level |  | IP65
Weight |  | <3kg
Dimensions |  | 300*170*80mm(L*W*H)
* Standard configuration. Different conditions under request, please consult Jutracker |  | 

## Slide 3
BiT Network Control Unit
Reliable Network
NCU
Mobile APP
Lora to BlueTooth
NCU.1 Lora Gateway
NCU.n Lora Gateway
TCU.1.1
TCU.1.2
TCU.1.n
n<=200
Transformer
Com Box.1
Transformer
Com Box.n
Wind Sensor.1
Wind Sensor.n
Solar Plant SCADA
GPRS/LTE4G
RS485
LORA
LORA
RS485
FIBER OPTICS
FIBER OPTICS
AC 220V
RS485
AC 220V
RS485
AC 220V from TRS
JuTracker Cloud Platform
LORA
DC 50V~200V from String
Control
Automatic
Manual
Network
Rain/Snow
Wind
Cleaning
O&M
Wireless
Plugin-Play
Operation Mode
Up to 200 TCU
Weather station
SCADA
© Jutracker Inc. Contents subject to change without notice. ALL RIGHTS RESERVED 2021 VER2.0
No 298 Kangyang Road, Xiangchen District, Suzhou, China | www.jutracker.com | sales@jutracker.com

## Slide 4
Jutracker
© Jutracker Inc. Contents subject to change without notice. ALL RIGHTS RESERVED 2021 VER2.0
No 298 Kangyang Road, Xiangchen District, Suzhou, China | www.jutracker.com | sales@jutracker.com
BiT-NCU
Network Control Unit Controller Electrical Specifications | NCU
Characteristic Parameters | 
Input | 
Power Supply | 220 VAC (L+N)
Control | 
Control Unit | High speed MCU
Tracking Accuracy | < ±1°
Parameters Setting | PC Software
Power Consumption | 
Daily Energy Consumption | <0.1 kWh/Day
Parameters Setting | 
GPS Signal | Yes
High Wind Trigger Threshold | PC
Heavy Snow Trigger Threshold | PC
Latitude and Longitude | Automatic
Time Zone (Winter Time) | Manual
Protection and Alarm | 
Weather Sensor Alarm | Yes
Communication Interruption With TCU | Yes
GPS Module Failure Alarm | Yes
Communication | 
Wireless Communication (with TCU) | LoRa
Protocol | Modbus
Environmental information | 
Wind Speed | Yes
Irradiation | Yes
Snow Thickness Information | Yes
General Data | 
Tracker Type | Jutracker BiT
Box Material | Q235B/Aluminum
Installation | Beam Hanging
Enclosure Testing | IP65
Weight | <6kg
Dimensions | 380*350*100mm(L*W*H)
Operation Temperature | -40° ~ 60°C<1)
Altitude | <3000m
* Standard configuration. Different conditions under request, please consult Jutracker |